SECTION 08 42 29.13

FOLDING AUTOMATIC ENTRANCES

Specifier Note: This specification document shall serve as a guide specification for typical projects where the Stanley Access Technologies folding automatic entrance, SB 600 Series, will be the basis of design. Specification must be reviewed for applicability on a per project basis. The specifier is directed to select appropriate options included herein. Consult with the local Access Technologies Territory Manager, when options, not specified, are required. See last page of this document for a summary of unspecified options.

- GENERAL

  - RELATED DOCUMENTS

    - Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 1 Specification Sections, apply to this Section.

  - SUMMARY

    - This Section includes the following types of folding automatic entrances:

      - Exterior and interior, folding automatic entrances with integral transoms.

      - Folding automatic entrances shall be configured as follows:

        - Four-Panel, Fold-In or Fold-Out.

        - Two-Panel, Fold-In or Fold-Out.

    - Related Sections:

      - Division 7 Sections for caulking to the extent not specified in this section.

      - Division 8 Section "Aluminum-Framed Entrances and Storefronts" for entrances furnished separately in Division 8 Section.

      - Division 8 Section "Door Hardware" for hardware to the extent not specified in this Section.

      - Division 8 Section Glazing for materials and installation requirements of glazing for automatic entrance doors.

      - Division 26 Sections for electrical connections including conduit and wiring for folding automatic entrance door operators.

  - REFERENCES

General: Standards listed by reference, including revisions by issuing authority, form a part of this specification section to extent indicated. Standards listed are identified by issuing authority, authority abbreviation, designation number, title or other designation established by issuing authority.  Standards subsequently referenced herein are referred to by issuing authority abbreviation and standard designation.

    - Underwriters Laboratories (UL):

      - UL 325 – Standard for Door, Drapery, Gate, Louver, and Window Operators and Systems.

    - American National Standards Institute (ANSI)/Builders’ Hardware Manufacturers Association (BHMA):

      - ANSI/BHMA A156.10: Standard for Power Operated Pedestrian Doors.

    - American Society for Testing and Materials (ASTM):

      - ASTM B221 - Standard Specification for Aluminum and Aluminum-Alloy Extruded Bars, Rods, Wire, Profiles, and Tubes.

      - ASTM B209 - Standard Specification for Aluminum and Aluminum-Alloy Sheet and Plate

    - Builders’ Hardware Manufacturers Association (BHMA):

      - BHMA A156.10 - Standard for Power Operated Pedestrian Doors.

    - American Association of Automatic Door Manufacturers (AAADM):

    - National Fire Protection Association (NFPA):

      - NFPA 101 – Life Safety Code.

      - NFPA 70 – National Electric Code.

    - International Code Council (ICC):

      - IBC: International Building Code

    - Building Officials and Code Administrators International (BOCA), 1999:

    - International Standards Organization (ISO):

      - ISO 9001 - Standard for Manufacturing Quality Management Systems

    - National Association of Architectural Metal Manufacturers (NAAMM):

      - Metal Finishes Manual for Architectural and Metal Products.

Specifier Note: Modify paragraph below to suit project requirements. - Select appropriate standard finish from options below. - Make multiple selections as required; schedule accordingly. - See last page of this document for a summary of unspecified finish options. - Coordinate with other sections.

    - American Architectural Manufacturers Association (AAMA):

      - [AAMA 606.1 – Integral Color Anodic Finishes for Architectural Aluminum.]

      - [AAMA 607.1 - Clear Anodic Finishes for Architectural Aluminum.]

      - AAMA 611 Voluntary Specification for Anodized Architectural Aluminum.

      - AAMA 701 Voluntary Specification for Pile Weatherstripping and Replaceable Fenestration Weatherseals.

  - DEFINITIONS

    - Activation Device:  Device that, when actuated, sends an electrical signal to the door operator to open the door.

    - Safety Device:  Device that prevents a door from opening or closing, as appropriate.

  - PERFORMANCE REQUIREMENTS

    - Provide folding automatic entrances capable of withstanding structural loads and thermal movements based on testing manufacturer's standard units in assemblies similar to those indicated for this Project.

    - Operating Range:  Minus 30 deg F (29 deg C) to 130 deg F (54 deg C).

    - Entrapment Protection: The force required to prevent a stopped door, in the last 10 degrees of the opening, from moving in the direction of opening shall not exceed 40 lbf (180 N) applied at 1” (25 mm) form the leading edge of the FS leaf.

    - Break Away Requirements: Folding automatic entrances provided with a breakaway device shall require no more than 50 lbf (222 N) applied at 1” (25 mm) from the latch edge of the door to break door panels out.  No header mounted stops, jamb mounted stops, or jamb mounted cams, shall be required for proper function of breakaway device. Breakaway system shall incorporate a disconnect switch to prevent powered operation while door is broken out.

  - SUBMITTALS

    - Submit listed submittals in accordance with Conditions of the Contract and Division 01 submittal procedures.

    - Shop Drawings:  Include plans, elevations, sections, details, hardware mounting heights, and attachments to other work. Indicate wiring for electrical supply.

    - Color Samples for selection of factory-applied color finishes.

    - Closeout Submittals: Provide the following with project close-out documents.

      - Owner’s Manual.

      - Warranties.

  - QUALITY ASSURANCE

    - Installer Qualifications:  Manufacturer's authorized representative, with certificate issued by AAADM, who is trained for installation and maintenance of units required for this Project.

    - Manufacturer Qualifications:  A qualified manufacturer with a manufacturing facility compliant with ISO 9001.

    - Manufacturer shall have in place a national service dispatch center providing 24 hours a day, 7 days a week, emergency call back service.

    - Certifications: Folding automatic entrances shall be certified by the manufacturer to meet performance design criteria in accordance with the following standards:

      - ANSI A156.10.

      - NFPA 101.

      - UL 325 Listed.

      - IBC.

      - BOCA.

    - Source Limitations:  Obtain folding automatic entrances through one source from a single manufacturer.

    - Product Options:  Drawings indicate sizes, profiles, and dimensional requirements of folding automatic entrances and are based on the specific system indicated. Do not modify intended aesthetic effects, as judged solely by Architect, except with Architect's approval. If modifications are proposed, submit comprehensive explanatory data to Architect for review.

    - Power Operated Door Standard: ANSI/BHMA A156.10.

    - Electrical Components, Devices, and Accessories:  Listed and labeled as defined in NFPA 70, Article 100, by a testing agency acceptable to authorities having jurisdiction, and marked for intended use.

    - Emergency-Exit Door Requirements:  Comply with requirements of authorities having jurisdiction for folding automatic entrance doors serving as a required means of egress.

  - PROJECT CONDITIONS

    - Field Measurements:  General Contractor shall verify openings to receive folding automatic entrances by field measurements before fabrication and indicate measurements on Shop Drawings.

    - Mounting Surfaces:  General Contractor shall verify all surfaces to be plumb, straight and secure; substrates to be of proper dimension and material.

    - Other trades:  General Contractor Advise of any inadequate conditions or equipment.

  - COORDINATION

    - Templates:  Check Shop Drawings of other work to confirm that adequate provisions are made for locating and installing folding automatic entrances to comply with indicated requirements.

    - Electrical System Roughing-in: Coordinate layout and installation of folding automatic entrances with connections to power supplies.

  - WARRANTY

    - Folding automatic entrances shall be free of defects in material and workmanship for a period of one (1) year from the date of substantial completion.

    - During the warranty period the Owner shall engage a factory-trained technician to perform service and affect repairs. A safety inspection shall be performed after each adjustment or repair and a completed inspection form shall be submitted to the Owner.

    - During the warranty period all warranty work, including but not limited to emergency service, shall be performed during normal working hours.

- PRODUCTS

  - FOLDING AUTOMATIC ENTRANCES

    - Manufacturer: Stanley Access Technologies; Bi-Fold SB 600 Series folding automatic entrance.

  - MATERIALS

    - Aluminum:  Alloy and temper recommended by manufacturer for type of use and finish indicated.

      - Headers, stiles, rails, and frames: 6063-T6

      - Extruded Bars, Rods, Profiles, and Tubes:  ASTM B 221.

      - Sheet and Plate:  ASTM B 209.

    - Sealants and Joint Fillers:  Performed under Division 7 Section "Joint Sealants".

  - AUTOMATIC ENTRANCE DOOR ASSEMBLIES

    - Provide manufacturer's standard folding automatic entrance assemblies including door panels, low profile hinges, framing, headers, door operators, electronic controllers, activation and safety devices, pivots, and accessories required for a complete installation.

    - Folding Automatic Entrance Doors:

      - Bi-Fold 620 Series

        - Configuration: Two-Panel, Fold-In or Fold-Out

        - Traffic Pattern:  Two-way.

        - Emergency Breakaway Capability: Full

        - Mounting:  Between jambs

      - Bi-Fold 640 Series

        - Configuration: Four-Panel, Fold-In or Fold-Out

        - Traffic Pattern:  Two-way.

        - Emergency Breakaway Capability: Full

        - Mounting:  Between jambs

  - COMPONENTS

    - Framing Members:  Manufacturer's standard extruded aluminum reinforced as required to support imposed loads.

      - Nominal Size: 1 ¾ inch by 4 ½ inch (45 by 115 mm).

    - Stile and Rail Door Panels:  Manufacturer's standard 1 3/4 inch (45 mm) thick glazed door panels with extruded-aluminum tubular stile and rail members. Incorporate concealed tie-rods that span full length of top and bottom rails or mechanically fasten corners with reinforcing brackets that are welded.

      - Glazing Stops and Gaskets:  Snap-on, extruded-security aluminum stops and preformed gaskets.

      - Hinge and Lock Stile Design: Narrow stile; 2 inch (51 mm) nominal width.

      - Fold Stile Design: Low profile; 1 inch (25 mm) nominal width.

      - Bottom Rail Design: Minimum 4 inch (102 mm) nominal height.

      - Muntin Bars: None.

    - Glazing:  Performed under Division 8 Section Glazing. All Glazing furnished by “by others” shall be 1/4 inch (6 mm) tempered, unless otherwise specified.

    - Header Case: Header case shall not exceed 6” (152 mm) square in section and shall be fabricated from extruded aluminum with structurally integrated end caps, designed to conceal door operators and controls. The operator shall be sealed against dust, dirt, and corrosion within the header case. Access to the operator and electronic control box shall be provided by a full-length removable cover, edge rabbetted to the header to ensure a flush fit.  Removable cover shall be secured to prevent unauthorized access.

    - Door Arm Assemblies: Door arm assembly shall consist of a forged steel arm which fastens into web of door panel top rail. All parts shall be concealed in the top web of the door. The door arm shall be splined to the operator drive spindle. The door arm assembly shall have no moving parts.

    - Thresholds: Manufacturer’s standard saddle type thresholds as indicated below:

      - Continuous standard tapered extrusion; double bevel.

      - All thresholds to conform to details and requirements for compliance with local codes.

    - Fasteners and Accessories:  Manufacturer's standard corrosion-resistant, non-staining, non-bleeding fasteners and accessories compatible with adjacent materials.

    - Signage:  Provide signage in accordance with ANSI/BHMA A156.10.

  - FOLDING DOOR OPERATORS

    - Provide door operators of size recommended by manufacturer for door size, weight, and movement; for condition of exposure; and for long-term, maintenance-free operation under normal traffic load for type of occupancy indicated.

    - Electromechanical Operators:  Self-contained unit powered by a minimum 3/16 horsepower, permanent-magnet DC motor; through a high torque reduction gear system.

      - Operation:  Power opening and spring closing.

      - Operator Type: Full energy.

      - Handing: Non-handed; no tools required to change handing.

      - Capacity: Rated for door panels weighing up to 350 lb (159 kg).

      - Mounting: Visible

      - Features:

        - Adjustable opening and closing speeds.

        - Adjustable opening and closing force.

        - Adjustable back-check.

        - Adjustable hold-open time between 0 and 30 seconds.

        - Reverse on obstruction.

        - Closed loop speed control with active braking and acceleration.

        - Variable obstruction recycle time delay.

        - Optional Switch to open/Switch to close operation.

    - Field Adjustable Spring Closing Operation: The operator shall close the door by spring energy employing the motor, as a dynamic brake to provide closing speed control. The closing spring shall be a helical compression spring, adjustable for positive closing action. The spring shall be adjustable, without removing the operator from the header, to accommodate a wide range of field conditions.

    - Independent Adjustable Closing and Latching Speed Control: The operator shall employ a rheostat module to allow for independent field adjustment of closing and latching speeds using the motor as a dynamic brake.

    - Field Adjustable Open Stop: The operator shall provide a field adjustable open stop to accommodate opening angles from 80 to 135 degrees without the need for additional components.

    - Consistent Cycle: The operator shall deliver an even, consistent open force across the entire transition from door fully closed to door fully open. Additionally, the range of the force shall be field adjustable to accommodate a wide range of on-site conditions.

    - Quiet Performance: The operator shall be designed to output audible noise ratios less than or equal to 50dba.

    - Electrical service to door operators shall be provided under Division 26 Electrical.  Minimum service to be 120 VAC, 5 amps.

  - ELECTRICAL CONTROLS

    - Electrical Control System: Electrical control system shall include a microprocessor controller and position encoder. The encoder shall monitor revolutions of the operator shaft and send signals to microprocessor controller to define door position. Systems utilizing external magnets and magnetic switches are not acceptable.

    - Performance Data: The microprocessor shall collect and store performance data as follows:

      - Counter: A non-resettable counter to track operating cycles.

      - Event Reporting: Unit shall include event and error recording including number of occurrences of events and errors, and cycle count of most recent events and errors.

      - LED Display: Display presenting the current operating state of the controller.

    - Controller Protection: The microprocessor controller shall incorporate the following features to ensure trouble free operation:

      - Automatic Reset Upon Power Up.

      - Main Fuse Protection.

      - Electronic Surge Protection.

      - Internal Power Supply Protection.

      - Resetable sensor supply fuse protection.

      - Motor Protection, over-current protection.

    - Soft Start/Stop: A “soft-start” “soft-stop” motor driving circuit shall be provided for smooth normal opening and recycling.

    - Obstruction Recycle: Provide system to recycle the folding panels when an obstruction is encountered during the closing cycle.

    - Programmable Controller: Microprocessor controller shall be field programmable.

      - The following parameters may be adjusted:

        - Operating speeds and forces as required to meet specified ANSI/BHMA standard.

        - Adjustable and variable features specified.

      - Manual programming shall be available through local interface which has a two-digit display with a selection control including three push buttons.

    - Emergency Breakout Switch: A cam actuated emergency breakout switch shall be provided to disconnect power to the motor when an in-swinging door is manually pushed in the emergency out direction. The operator will then automatically reset and power will be resumed.

  - ACTIVATION AND SAFETY DEVICES

    - Motion Sensors:  Motion sensors shall be mounted on the approach side of door to detect pedestrians in the activating zone, and provide a signal to open doors. Units shall incorporate K-band microwave frequency to detect all motion in the activation zone.  Units shall be configurable for wide or narrow activation zones and shall be suitable for mounting heights up to 13 feet (4 m).  Motion sensors shall be equal to or better than Stanley Access Technologies SU-100.

    - Overhead Presence Detection Sensors: Provide overhead presence detection sensors designed to sense pedestrians in the safety zone with the entrance fully open or fully closed. Overhead presence detection sensors shall be diffused active infrared type capable of sensing moving or stationary targets within the safety zone. Sensors shall be designed to function at mounting heights up to 9 feet (2.7 m) and shall be mounted on the fold side. Sensors detection patterns shall be programmable to accommodate various door and environmental conditions. Supporting relays shall be provided for a complete working system.

    - Presence Sensor Monitoring: Folding automatic entrances control system shall include a means to verify the functionality of all active presence sensors in accordance with ANSI/BHMA A156.10. A detected fault shall cause automatic operation to cease until the fault is corrected.

    - Guide Rails: Guide rails shall be provided manufactured from 1/2 inch x 1/2 inch (12 mm x 12 mm) T-6063 alloy aluminum. Length and height shall be minimum 36 inch x 36 inch (914 mm x 914 mm) and shall comply with requirements of ANSI A156.10. Finish shall match finish of folding automatic entrance.

    - Door Panel Safety:  Provide door panel safety systems as indicated below:

      - Silicone rubber finger guards at pivot stiles and at folding panels.

      - Neoprene safety seals at lead edge of door panels.

  - HARDWARE

    - Provide units in sizes and types recommended by automatic entrance door and hardware manufacturers for entrances and uses indicated.

    - Deadlocks:  Manufacturer's standard deadbolt operated by exterior cylinder and interior thumb turn; with minimum 1 inch (25 mm) long throw bolt; ANSI/BHMA A156.5, Grade 1.

      - Cylinders: Provide BEST lock cylinders, with core and key.

      - Hook Latch: Laminated-steel hook, mortise type, BHMA A156.5, Grade 1.

      - Two-Point Locking: Provide locking system that incorporates a device in the stile of active door leaves that automatically extends a flush bolt into the threshold.

    - Control Switch: Provide manufacturer’s standard jamb mounted rocker switches to allow for full control of the folding automatic entrance.  Controls to include, but are not limited to:

      - Power On/Off

      - On/Off/Hold-Open

    - Weather Stripping:  Manufacturer's standard replaceable components complying with AAMA 701; made of wool, polypropylene, or nylon woven pile with nylon-fabric or aluminum-strip backing.

    - Weather Sweeps:  Manufacturer's standard adjustable nylon brush sweep mounted to underside of door bottom.

  - FABRICATION

    - Factory fabricate folding automatic entrance components to designs, sizes, and thickness indicated and to comply with indicated standards.

      - Form aluminum shapes before finishing.

      - Use concealed fasteners to greatest extent possible.

        - Where fasteners are subject to loosening or turning out from thermal and structural movements, wind loads, or vibration, use self-locking devices.

        - Reinforce members as required to receive fastener threads.

    - Framing:  Provide folding automatic entrances as prefabricated assemblies.

      - Fabricate tubular and channel frame assemblies with manufacturer's standard mechanical or welded joints.  Provide sub-frames and reinforcement as required for a complete system to support required loads.

      - Perform fabrication operations in manner that prevents damage to exposed finish surfaces.

      - Form profiles that are sharp, straight, and free of defects or deformations.

      - Prepare components to receive concealed fasteners and anchor and connection devices.

      - Fabricate components with accurately fitted joints with ends coped or mitered to produce hairline joints free of burrs and distortion.

    - Door Panels:  Factory fabricated and assembled in profiles indicated. Reinforce as required to support imposed loads and for installing hardware.

    - Door Operators:  Factory fabricated and installed in headers, including testing.

    - Glazing:  Fabricate framing with minimum glazing edge clearances for thickness and type of glazing indicated.

    - Hardware:  Factory install hardware to the greatest extent possible; remove only as required for final finishing operation and for delivery to and installation at Project site.

  - ALUMINUM FINISHES

    - Comply with NAAMM Metal Finishes Manual for Architectural and Metal Products for recommendations for applying and designing finishes. Finish designations prefixed by AA comply with system established by Aluminum Association for designing finishes.

Specifier Note: Modify paragraph below to suit project requirements. - Select appropriate standard finish from options below. - Make multiple selections as required; schedule accordingly. - See last page of this document for a summary of unspecified finish options.

    - [Class II, Clear Anodic Finish: AA-M12C22A31 Mechanical Finish: as fabricated; Chemical Finish: etched, medium matte; Anodic Coating: Architectural Class II, clear coating 0.40 mils minimum complying with AAMA 611-98, and the following:

      - AAMA 607.1

      - Applicator must be fully compliant with all applicable environmental regulations and permits, including wastewater and heavy metal discharge.]

    - [Class I, Color Anodic Finish: AA-M12C22A42/A44 Mechanical Finish: as fabricated; Chemical Finish: etched, medium matte; Anodic Coating: Architectural Class I, integrally colored or electrolytically deposited color coating 0.70 mils minimum complying with AAMA 611-98, and the following:

      - Color: Dark Bronze.

      - AAMA 606.1

      - Applicator must be fully compliant with all applicable environmental regulations and permits, including wastewater and heavy metal discharge.]

- EXECUTION

  - INSPECTION

Examine conditions, with Installer present, for compliance with requirements for installation tolerances, header support, and other conditions affecting performance of folding automatic entrance doors. Proceed with installation only after unsatisfactory conditions have been corrected.

  - INSTALLATION

    - Do not install damaged components.  Fit joints to produce hairline joints free of burrs and distortion. Rigidly secure non-movement joints.

    - Mounting:  Install folding automatic entrances/headers plumb and true in alignment with established lines and grades.  Anchor securely in place.

      - Install surface-mounted hardware using concealed fasteners to greatest extent possible.

      - Set headers, arms and linkages level and true to location with anchorage for permanent support.

    - Door Operators:  Connect door operators to electrical power distribution system as specified in Division 26 Sections.

    - Glazing:  Performed under Division 8 Section "Glazing" in accordance with folding automatic entrance manufacturer’s instructions.

    - Sealants:  Comply with requirements specified in Division7 Section "Joint Sealants".

  - FIELD QUALITY CONTROL

    - Testing Services:  Factory Trained Installer shall test and inspect each folding automatic entrance door to determine compliance of installed systems with applicable ANSI standards.

  - ADJUSTING

    - Adjust door operators, controls, and hardware for smooth and safe operation, for tight closure, and complying with requirements in ANSI/BHMA A156.10 by AAADM Certified Technician.

  - CLEANING AND PROTECTION

    - Clean surfaces promptly after installation.  Remove excess sealant compounds, dirt, and other substances.  Repair damaged finish to match original finish.

END OF SECTION 08 42 29.13 [08460]

Available options not specified in this document are summarized as follows:

Integral transoms, with optional number and placement of verticals.

Various threshold configurations (Continous Double Bevel threshold specified).

Finish (Class 2, Clear Anodized specified) options include:

Standard color anodizing options.

Multi-coat Fluoropolymer painted finishes.

Bottom rail and muntin options for door panels.

Glazing options to 1” thick.

Contact your local Stanley Access Technologies representative for more information on specifying the right folding automatic entrance for your project.

These specifications represent a “sample” configuration and depict design features that are commonly used. These specifications do not reflect “standard” features and are provided for informational purposes only. Please note that there is no standard “off the shelf” product.  Stanley custom manufactures each product to its customers’ specifications. It is the customer’s responsibility to validate that a particular configuration of Stanley’s products is suitable for a specific application.  All specifications and designs contained herein are subject to change without notice or obligation.