This product has received a verified Environmental Product Declaration (EPD) based on a North American Product Category Rule (PCR.)

SECTION 08 42 43

INTENSIVE CARE UNIT/CRITICAL CARE UNIT ENTRANCES

Specifier Note: This specification document shall serve as a guide specification for typical projects where the Stanley Access Technologies ProCare 8300 Series ICU/CCU entrance will be the basis of design. Specification must be reviewed for applicability on a per project basis. The specifier is directed to select appropriate options included herein. Consult with the local Access Technologies Territory Manager, when options, not specified, are required. See last page of this document for a summary of unspecified options.

- GENERAL

  - RELATED DOCUMENTS

    - Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 1 Specification Sections, apply to this Section.

  - SUMMARY

    - This Section includes the following types of intensive care unit/critical care unit (ICU/CCU) entrances:

      - Interior, single slide, manual sliding ICU/CCU entrances; trackless.

      - Entrances shall be rated as an effective barrier limiting the passage of smoke.

    - Related Sections:

      - Division 7 Sections for caulking to the extent not specified in this section.

      - Division 8 Section "Door Hardware" for hardware to the extent not specified in this Section.

      - Division 8 Section Glazing for materials and installation requirements of glazing for ICU/CCU entrances.

      - Division 26 Sections for electrical connections including conduit and wiring for grounding of ICU/CCU entrances.

  - REFERENCES

    - General: Standards listed by reference, including revisions by issuing authority, form a part of this specification section to extent indicated. Standards listed are identified by issuing authority, authority abbreviation, designation number, title or other designation established by issuing authority.  Standards subsequently referenced herein are referred to by issuing authority abbreviation and standard designation.

    - American National Standards Institute (ANSI) / Builders’ Hardware Manufacturers Association (BHMA):

      - ANSI A117.1: Accessible and Usable Buildings and Facilities

    - American Society for Testing and Materials (ASTM):

      - ASTM B221 - Standard Specification for Aluminum and Aluminum-Alloy Extruded Bars, Rods, Wire, Profiles, and Tubes.

      - ASTM B209 - Standard Specification for Aluminum and Aluminum-Alloy Sheet and Plate

    - International Organization for Standardization (ISO):

      - ISO 9001 - Quality Management Systems

      - ISO 14025 – Environmental Labels and Declarations -- Type III Environmental Declarations -- Principles and Procedures

      - ISO14040 – Environmental Management -- Life Cycle Assessment -- Principles and Framework

      - ISO 14044 – Environmental Management -- Life Cycle Assessment -- Requirements and Guidelines

      - ISO 21930 – Sustainability in Buildings and Civil Engineering Works -- Core Rules For Environmental Product Declarations Of Construction Products And Services

    - National Fire Protection Association (NFPA):

      - NFPA 105 – Standard for the Installation of Smoke Door Assemblies

    - Underwriters Laboratories (UL):

      - UL 1784 – Air Leakage Tests for Door Assemblies

    - National Association of Architectural Metal Manufacturers (NAAMM):

      - Metal Finishes Manual for Architectural and Metal Products.

    - American Architectural Manufacturers Association (AAMA):

      - AAMA 607.1 - Clear Anodic Finishes for Architectural Aluminum.

      - AAMA 701 Voluntary Specification for Pile Weatherstripping and Replaceable Fenestration Weatherseals.

    - United Nations Central Product Classification (UNCPC):

      - UNCPC 4212 - Product Category Rules for Preparing an Environmental Product Declaration for Power-Operated Pedestrian Doors and Revolving Doors.

  - PERFORMANCE REQUIREMENTS

    - General:  Provide ICU/CCU entrances capable of withstanding structural loads and thermal movements based on testing manufacturer's standard units in assemblies similar to those indicated for this Project.

    - Operating Range:  Minus 30 deg F (Minus 34 deg C) to 130 deg F (54 deg C).

    - Smoke and Draft Control: Provide smoke and draft control system on ICU/CCU entrances.  Smoke and draft control system shall provide an effective barrier for limiting the passage of smoke. Smoke and draft control system shall comply with the following:

      - Air Leakage Rates: The maximum air leakage rate for ICU/CCU entrances shall be as follows:

        - Tested without artificial bottom seal, at 0.10 in water column (25 Pa), leakage shall be less than 2.5 ft3/min/ft2 (0.8 m3/min/m2) of framed opening at ambient temperature; and, less than 1.0 ft3/min/ft2 (0.3 m3/min/m2) of framed opening at elevated temperature.

        - Tested with artificial bottom seal, at 0.30 in water column (75 Pa), leakage shall be less than 2.0 ft3/min/ft2 (0.6 m3/min/m2) of framed opening at ambient temperature; and, less than 1.0 ft3/min/ft2 (0.3 m3/min/m2) of framed opening at elevated temperature.

      - Door shall be tested in accordance UL 1784.

      - Installation shall be in accordance with NFPA 105.

    - Opening Force: Force required to slide ICU/CCU entrances to the full open position shall not exceed 5 lb (22.2 N) in accordance with ANSI A117.1.

  - SUBMITTALS

    - General:  Submit the following in accordance with Conditions of the Contract and Division 1 Specification Sections.

    - Shop Drawings:  Include plans, elevations, sections, details, hardware mounting heights, and attachments to other work.

    - Color Samples for selection of factory-applied color finishes.

    - Closeout Submittals:

      - Owner’s Manual.

      - Warranties.

    - Reports:  Based on evaluation performed by a qualified agency, for ICU/CCU entrance door assemblies.

      - Environmental Product Declaration.

  - QUALITY ASSURANCE

    - Installer Qualifications:  Manufacturer's authorized representative, with certificate issued by AAADM, who is trained for installation and maintenance of units required for this Project.

    - Manufacturer Qualifications:  A qualified manufacturer with a manufacturing facility compliant with ISO 9001.

    - Manufacturer shall have in place a national service dispatch center providing 24 hours a day, 7 days a week, emergency call back service.

    - Certifications: ICU/CCU entrances provided as an effective barrier against the passage of smoke shall be UL 1784 listed.

    - Environmental Product Declaration (EPD): EPD for automatic sliding entrances shall be certified by the manufacturer to comply with the following:

      - Prepared under Product Category Rule (PCR) UNCPC 4212.

      - Conform to ISO standards 14025, 14040, 14044, 21930.

      - Life Cycle Assessment Basis: Cradle to Gate, minimum.

    - Source Limitations:  Obtain ICU/CCU entrances through one source from a single manufacturer.

    - Product Options:  Drawings indicate sizes, profiles, and dimensional requirements of ICU/CCU entrances and are based on the specific system indicated.  Refer to Division 1 Section "Product Requirements."

  - PROJECT CONDITIONS

    - Field Measurements:  General Contractor shall verify openings to receive ICU/CCU entrances by field measurements before fabrication and indicate measurements on Shop Drawings.

    - Mounting Surfaces: General Contractor shall verify all surfaces to be plumb, straight and secure; substrates to be of proper dimension and material.

    - Other trades:  General Contract shall advise of any inadequate conditions or equipment.

  - COORDINATION

    - Templates:  Check Shop Drawings of other work to confirm that adequate provisions are made for locating and installing ICU/CCU entrances to comply with indicated requirements.

    - Electrical System Roughing-in: Coordinate layout and installation of ICU/CCU entrances with connections to facility grounding system.

  - WARRANTY

    - ICU/CCU entrances shall be free of defects in material and workmanship for a period of one (1) year from the date of substantial completion.

    - During the warranty period the Owner shall engage a factory-trained technician to perform service and affect repairs. A safety inspection shall be performed after each adjustment or repair and a completed inspection form shall be submitted to the Owner.

    - During the warranty period all warranty work, including but not limited to emergency service, shall be performed during normal working hours.

- PRODUCTS

  - ICU/CCU ENTRANCES

    - Manufacturer: Stanley Access Technologies; ProCare™ 8300 Series manual sliding ICU/CCU entrances.

  - MATERIALS

    - Aluminum:  Alloy and temper recommended by manufacturer for type of use and finish indicated.

      - Headers, stiles, rails, and frames 6063-T6

      - Extruded Bars, Rods, Profiles, and Tubes:  ASTM B 221.

      - Sheet and Plate:  ASTM B 209.

    - Sealants and Joint Fillers:  Performed under Division 7 Section "Joint Sealants".

  - ICU/CCU ENTRANCE ASSEMBLIES

    - General:  Provide manufacturer's standard ICU/CCU entrance assemblies including doors, sidelights, framing, headers, carrier assemblies, roller tracks, pivots, and accessories required for a complete installation.

Specifier Note: Modify paragraph below to suit project requirements. Coordinate with other sections. - 7/8 inch jambs are required to achieve maximum clear door opening.

    - ICU/CCU Entrances:

      - Configuration: One sliding panel and one full sidelight; single slide.

      - Traffic Pattern:  Two-way [providing 44 inch (1118 mm) clear sliding opening with an overall frame width of 96 inch (2438 mm)].

      - Breakaway Capability: Sliding panels and sidelights, from fully open position.

      - Mounting:  Between jambs.

      - Track: None, trackless.

  - COMPONENTS

Specifier Note: Modify paragraph below to suit project requirements. Coordinate with other sections. - Standard size is 7/8 inch by 4 1/2 inch; 1 3/4 inch by 4 1/2 inch is optional. 7/8 inch jambs are required to achieve maximum clear door opening specified in 2.3, B, 2. - “Concealed Fastening” is optional; standard jambs have rectangular section.

    - Framing Members:  Manufacturer's standard extruded aluminum reinforced as required to support imposed loads.

      - Nominal size shall be [7/8 inch] [1 3/4 inch] by 4 1/2 inch ([22 mm] [44 mm] by 115 mm).

      - [Concealed Fastening: Framing shall incorporate a concealed fastening pocket, and continuous flush insert cover, extending full length of each framing member.]

Specifier Note: Modify paragraph below to suit project requirements. - Select “Bottom Rail Design”; 4 inch is standard. - Select “Muntin Bars”; 2 inch is standard.

    - Stile and Rail Doors and Sidelights:  Manufacturer's standard 1 ¾ inch (45 mm) thick glazed doors with extruded-aluminum tubular stile and rail members. Incorporate concealed tie-rods that span full length of top and bottom rails.

      - Glazing Stops and Gaskets:  Snap-on, extruded-security aluminum stops and preformed gaskets.

      - Stile Design: Narrow stile; up to 2 1/8 inch (54 mm) nominal width.

      - Bottom Rail Design:  Minimum [4 inch (102 mm)] [6 inch (152 mm)] [8 inch (203 mm)] [10 inch (254 mm)] [12 inch (305 mm)] nominal height.

      - Muntin Bars:  [None.] [Horizontal tubular rail member for each door; [2 inch (51 mm)] [4 1/4 inch (108 mm)] nominal height.]

Specifier Note: Modify paragraph below to suit project requirements. 1/4 inch Tempered glass is standard; privacy glazing with integral blinds is optional.

    - Glazing: Furnished under Division 8 Section Glazing. All Glazing furnished under separate section shall be [1/4 inch (6 mm) tempered] [privacy glazing, [1 inch (25 mm)] insulated with integral blinds].

    - Headers:  Fabricated from extruded aluminum and extending full width of ICU/CCU entrance units to conceal carrier assemblies, and roller tracks.  Provide hinged or removable access panels for service and adjustment of door carrier assemblies.  Secure panels to prevent unauthorized access. Mounting shall be concealed, with one side of header flush with framing.

    - Carrier Assemblies and Overhead Roller Tracks:  Manufacturer's standard carrier assembly that allows vertical adjustment of at least 1/8 inch (3 mm); consisting of urethane with precision steel lubricated ball-bearing wheels, operating on a continuous roller track. Support panels from carrier assembly by load wheels and anti-rise mechanism with factory adjusted cantilever and pivot assembly. Minimum two ball-bearing load wheels for each active leaf. Minimum load wheel diameter shall be 2 1/2 inch (64 mm).

    - Fasteners and Accessories:  Manufacturer's standard corrosion-resistant, non-staining, non-bleeding fasteners and accessories compatible with adjacent materials.

  - HARDWARE

    - General:  Provide units in sizes and types recommended by ICU/CCU entrance and hardware manufacturers for entrances and uses indicated.

    - Breakaway Feature:  Provide release hardware that allows sliding panel and sidelight to swing out in direction of egress to full 90 degrees, only from the fully open position.

      - Latching system shall allow both panels to swing out after disengaging semi-automatic flush bolt from a single release point.

      - When returning panels from breakaway position, panels shall self-latch.

    - Positive Latch:  Manufacturer's standard non-keyed, spring loaded, latch and strike that can secure sliding door panels to adjacent panels or jambs. Strike shall mount flush to surface of framing. Latch shall engage by closing action of door.

      - Dead latch hook bolt shall be concealed to prevent snagging.

      - Handle shall be circumferential design without exposed edges or open ends.

      - Handle action shall be linear, unlatching in the direction of slide.

    - Smoke Seal Components: Provide manufactures standard smoke and draft control components as required to meet performance specifications.  Components included but are not limited to:

      - High temperature seals.

      - Stiles shall be slotted for seal mounting.

  - FABRICATION

    - General:  Factory fabricate ICU/CCU entrance components to designs, sizes, and thickness indicated and to comply with indicated standards.

      - Form aluminum shapes before finishing.

      - Use concealed fasteners to greatest extent possible.

        - Where fasteners are subject to loosening or turning out from thermal and structural movements, wind loads, or vibration, use self-locking devices.

        - Reinforce members as required to receive fastener threads.

    - Framing:  Provide ICU/CCU entrances as prefabricated assemblies.

      - Fabricate tubular and channel frame assemblies with manufacturer's standard mechanical or welded joints.  Provide sub-frames and reinforcement as required for a complete system to support required loads.

      - Perform fabrication operations in manner that prevents damage to exposed finish surfaces.

      - Form profiles that are sharp, straight, and free of defects or deformations.

      - Prepare components to receive concealed fasteners and anchor and connection devices.

      - Fabricate components with accurately fitted joints with ends coped or mitered to produce hairline joints free of burrs and distortion.

    - Doors:  Factory fabricated and assembled in profiles indicated. Reinforce as required to support imposed loads and for installing hardware.

    - Glazing:  Fabricate framing with minimum glazing edge clearances for thickness and type of glazing indicated.

    - Hardware:  Factory install hardware to the greatest extent possible; remove only as required for final finishing operation and for delivery to and installation at Project site.

  - ALUMINUM FINISHES

    - General: Comply with NAAMM Metal Finishes Manual for Architectural and Metal Products for recommendations for applying and designing finishes. Finish designations prefixed by AA comply with system established by Aluminum Association for designing finishes.

    - Class II, Clear Anodic Finish: AA-M12C22A31 Mechanical Finish: as fabricated; Chemical Finish: etched, medium matte; Anodic Coating: Architectural Class II, clear coating 0.40 mils minimum complying with AAMA 611-98, and the following:

      - AAMA 607.1

      - Applicator must be fully compliant with all applicable environmental regulations and permits, including wastewater and heavy metal discharge.

- EXECUTION

  - INSPECTION

    - Examine conditions for compliance with requirements for installation tolerances, header support, and other conditions affecting performance of ICU/CCU entrances. Proceed with installation only after unsatisfactory conditions have been corrected.

  - INSTALLATION

    - General:  Do not install damaged components.  Fit frame joints to produce joints free of burrs and distortion. Rigidly secure non-movement joints.

    - Entrances:  Install ICU/CCU entrances plumb and true in alignment with established lines and grades without warp or rack of framing members and doors.  Anchor securely in place.

      - Install surface-mounted hardware using concealed fasteners to greatest extent possible.

      - Set headers, carrier assemblies, tracks, operating brackets, and guides level and true to location with anchorage for permanent support.

    - Grounding:  Connect ICU/CCU entrances to building grounding system as specified in Division 26 Sections.

    - Glazing: Performed under Division 8 Section "Glazing" in accordance with ICU/CCU entrance manufacturer’s instructions.

    - Sealants:  Comply with requirements specified in Division7 Section "Joint Sealants".

  - FIELD QUALITY CONTROL

    - Testing Services:  Factory Trained Installer shall test and inspect each ICU/CCU entrance to determine compliance of installed systems with applicable standards.

  - ADJUSTING

    - Adjust ICU/CCU entrances, and hardware for smooth and safe operation.

  - CLEANING AND PROTECTION

    - Clean glass and aluminum surfaces promptly after installation.  Remove excess glazing and sealant compounds, dirt, and other substances.  Repair damaged finish to match original finish. Comply with requirements in Division 8 Section “Glazing”, for cleaning and maintaining glass.

END OF SECTION 08 42 43

Available options not specified in this document are summarized as follows:

Finish (Class 2, Clear Anodized specified) options include:

Standard color anodizing options.

Multi-coat Fluoropolymer painted finishes.

Rail and muntin options for sliding and fixed door panels.

Jamb Options (7/8” x 4 ½” Rectangular Specified)

7/8” x 4 ½” Rectangular Jamb with Fastening Pocket.

1 3/4” x 4 ½” Rectangular Jamb.

1 3/4” x 4 ½” Rectangular Jamb with Fastening Pocket.

Glazing options (1/4” tempered specified) include:

Support for installation of privacy glazing with integral blinds up to 1” thick.

1 ¼” thick privacy glazing solutions are supported with universal glass stops by privacy glazing manufacturer.

Locking options (Positive Latch specified); 1-Point lock.

Standard: Keyed cylinder by Thumb Turn

Dummy cylinders optional

Lock positon indicator optional

Anti-Microbial coating on “Touch Points” or full package.

Integrated self-closing device with hold open.

Package Types Available:

Smoke & Draft Package, specified.

Isolation Package (Pressure Control System).

STC-Rated Package

Contact your local Stanley Access Technologies representative for more information on specifying the right sliding automatic entrance for your project.

These specifications represent a “sample” door configuration and depict design features that are commonly used. These specifications do not reflect “standard” features and are provided for informational purposes only. Please note that there is no standard “off the shelf” product.  Stanley custom manufactures each product to its customers’ specifications. It is the customer’s responsibility to validate that a particular configuration of Stanley’s products is suitable for a specific application.  All specifications and designs contained herein are subject to change without notice or obligation.